## Introduction
Machinery Room Ventilation Analysis Tool
Version: | 2.41
Overview: | The idea and the majority of the work for developing a ventilation analysis tool to determine if ventilation systems met the codes and standards at the time the ventilation system was built was provided by Ron Worley. More than 2000 hours was put into research to find the applicable codes and standards and the development of the tool. Doug Reindl collaborated and provided expertise on this project and also led the peer review with eight registered professional engineers. Ventilation is an important safety system for machinery rooms that house industrial refrigeration systems. Machinery room ventilation systems provide a number of functions that can be categorized based on the operating modes identified below. Key aspects of the ventilation design requirements found in one commonly used design standard for industrial refrigeration systems, IIAR 2, are summarized later in this document. This ventilation analysis tool includes anhydrous ammonia as one of the refrigerant choices. Some facilities using anhydrous ammonia may be subject to regulatory requirements such as OSHA's Process Safety Management (PSM) standard [29 CFR 1910.119] as well as EPA's Risk Management Program [40 CFR Part 68]. For those covered processes, employers/operators are required to document the design and design basis for their machinery room ventilation systems [see 29 CFR 1910.119(d)(3)(i)(E) and 40 CFR 68.65(d)(1)(v)]. The intent of this tool is to provide sufficient information to serve as the basis for documenting the ventilation systems for machinery rooms housing such covered processes. Included in the latter sections of this spreadsheet is a summary of the key ventilation requirements given in IIAR 2 (provided with permission from IIAR). The specific requirements for machinery room ventilation in other codes and standards can be obtained by contacting the relevant code/standard developer. For the IMC, contact the International Code Council (www.iccsafe.org). For , Standard 15, contact ASHRAE (www.ashrae.org). For the UMC and CMC, contact IAPMO (www.iapmo.org). For Canadian Standards Association (CSA) B52, contact CSA (www.csa.ca). Collectively, these documents establish what OSHA refers to as industry Recognized as Generally Accepted Good Engineering Practices (RAGAGEP). It is important to keep in mind that codes and standards are not static but frequently change. In many cases, changes to codes and standards do not retroactively apply the updated or new requirements to existing systems. Although an existing system may not be subject to these revised or new requirements, it is important for owners and design professionals to consider whether implementing the revised requirements to an existing system will materially enhance safety. In that case, a business decision may prompt the upgrade. Finally, codes and standards will dictate that revised requirements must be implemented when substantive changes are made to a machinery room or system. The summaries included in this spreadsheet are NOT necessarily all inclusive with the controls and other design requirements related to machinery room ventilation systems (e.g. discharge locations, etc.). This spreadsheet is focused on the calculations related to both non-emergency and emergency ventilation requirements for machinery rooms using ammonia and other refrigerants. Users of this tool must carefully review the information provided in the "DISCLAIMER" tab of this tool prior to its use.
Summary: | This spreadsheet is intended to summarize ventilation rate requirements for industrial refrigeration machinery rooms using ammonia and/or non-ammonia refrigerants. It allows users to input information for a given machinery room being evaluated and it compares actual installed equipment with codes and standards requirements based on the user's selected codes or standards that are or were in force for the location at the time of installation. The non-emergency ventilation rate calculations for temperature control assume all equipment within the space, as-noted, is operating and producing heat. As such, the ventilation rate is based on a peak load of operable equipment within the space. The tool allows "standby" equipment to be documented; however, equipment listed only in the "standby" category are not included in the peak heat load for the non-emergency ventilation rate calculations.
Machinery Room ventilation modes of operation: | - Emergency - Non-emergency Intermittent, or Normal (also known as Temperature Control) - Non-emergency Occupied, or Minimum Occupied
Sensor
Roof line
Relief Vent Main
Relief Vent
Run
-
outs
L
Exhaust
Fan
Z
L
NH3
Sensor
Panel
25 ppm
Electrical
Shutdown

## DISCLAIMER
Machinery Room Ventilation Analysis Tool
Version: | 2.41
DISCLAIMER: | DISCLAIMER OF WARRANTIES AND LIMITATION OF LIABILITIES: THERE WERE MULTIPLE CONTRIBUTORS TO THE DEVELOPMENT OF THIS TOOL. EVERY EFFORT WAS MADE TO ENSURE THE CONTENTS CONTAINED AND THE RESULTS PROVIDED BY THIS SPREADSHEET ARE ACCURATE; HOWEVER, THE FOLLOWING APPLIES: A. THIS SPREADSHEET IS OFFERED WITHOUT ANY WARRANTY OR REPRESENTATION WHATSOEVER, EXPRESS, OR IMPLIED, I. WITH RESPECT TO THE USE OF ANY INFORMATION, APPARATUS, METHOD, PROCESS OR SIMILAR ITEM DISCLOSED IN THIS FILE, INCLUDING MERCHANTABILITY AND FITNESS FOR A PARTICULAR PURPOSE, II. THAT SUCH USE DOES NOT INFRINGE ON OR INTERFERE WITH PRIVATELY OWNED RIGHTS, INCLUDING ANY PARTY'S INTELLECTUAL PROPERTY, III. THAT THE ANALYSIS OR RESULTS ARE SUITABLE TO ANY PARTICULAR USER'S CIRCUMSTANCE; B. THE CONTRIBUTORS TO THE DEVELOPMENT OF THIS SPREADSHEET ASSUME NO RESPONSIBILITY FOR ANY DAMAGES OR OTHER LIABILITY WHATSOEVER (INCLUDING ANY CONSEQUENTIAL DAMAGES, EVEN IF THE DEVELOPERS OR THEIR IRC REPRESENTATIVES HAS BEEN ADVISED OF THE POSSIBILITY OF SUCH DAMAGES) RESULTING FROM YOUR SELECTION OR USE OF THIS TOOL OR ANY INFORMATION, RESULT, METHOD, PROCESS, APPARATUS, OR SIMILAR ITEM DISCLOSED IN THIS FILE. C. THE CONTENTS AND DETAILS OF THIS VENTILATION SPREADSHEET MAY CHANGE FROM TIME TO TIME AND WITHOUT NOTICE. THIS VERSION OF THE SPREADSHEET MAY NOT BE THE LATEST. THE USER OF THIS TOOL TAKES FULL RESPONSIBILITY FOR THE RESULTS PRODUCED, INTERPRETATION OF RESULTS PRODUCED AND FOR THE APPLICATION OF RESULTS PRODUCED BY THIS TOOL. D. THE INFORMATION PRESENTED IN THIS TOOL ARE NOT INTENDED TO SERVE AS FORMAL OR INFORMAL INTREPRETATIONS TO ANY RELATED CODE OR STANDARDS. IF INTERPERPRATION OF SPECIFIC REQUIREMENTS APPEARING IN ANY CODE OR STANDARD IS NECESSARY, THE STANDARD OR CODE DEVELOPER SHOULD BE SOUGHT DIRECTLY FOR THE SAME.

## Ventilation Evaluation
Ventilation System Comparative Evaluation
Facility Name: |  | 0 |  |  | Date: | 0
The Code or Standard selected for Ventilation Installed vs. Design Basis Comparison: |  |  |  |  | IIAR 2-2021 (2021-Present)
Room Name: |  | 0 |  | Refrigerant Evaluated: | 0
| Normal (Temperature Control) Ventilation: |  | Are all Normal Exhaust Fans Non-Sparking Construction? | N/A | Do all Normal Exhaust Fans Discharge Up with Minimum 2500 FPM Velocity? |  | N/A
| Installed Normal Exhaust Air: |  |  | 0 | ft3 / min | 0 | l/s
| Design Basis Normal: |  | (104°F max temp) | 0 | ft3 / min | 0 | l/s
| Normal Exhaust Air Exceeds Minimum by: |  |  | 0 | ft3 / min | 0 | l/s
| Installed Normal Supply Air: |  |  | 0 | ft3 / min | 0 | l/s
| Check Negative Pressure - Supply Fan Air Exceeds Exhaust Fan Air by: |  |  | 0 | ft3 / min | 0 | l/s
| Continuous (Occupant) Ventilation: |  | Are all Continuous Exhaust Fans Non-Sparking Construction? | N/A | Do all Continuous Exhaust Fans Discharge Up with Minimum 2500 FPM Velocity? |  | N/A
| Installed Continuous Exhaust Air: |  |  | 0 | ft3 / min | 0 | l/s
| Design Basis Continuous: |  | (20 CFM/person when occupied) | 0 | ft3 / min | 0 | l/s
| Continuous Ventilation Exceeds Minimum by: |  |  | 0 | ft3 / min | 0 | l/s
| Installed Continuous Supply Air: |  |  | 0 | ft3 / min | 0 | l/s
| Check Negative Pressure - Supply Fan Air Exceeds Exhaust Fan Air by: |  |  | 0 | ft3 / min | 0 | l/s
| Emergency Ventilation: |  | Are all Emergency Exhaust Fans Non-Sparking Construction? | Not Known | Do all Emergency Exhaust Fans Discharge Up with Minimum 2500 FPM Velocity? |  | Not Known
| Installed Emergency Exhaust Air: |  |  | 0 | ft3 / min | 0 | l/s
| Design Basis Emergency: |  | N/A | 0 | ft3 / min | 0 | l/s
|  |  | (30 ACH) | 0 | ft3 / min | 0 | l/s
| Emergency Exhaust Air Exceeds Minimum by: |  |  | 0 | ft3 / min | 0 | l/s
| Installed Emergency Supply Air: |  |  | 0 | ft3 / min | 0 | l/s
| Check Negative Pressure - Supply Fan Air Exceeds Exhaust Fan Air by: |  |  | 0 | ft3 / min | 0 | l/s
Prepared By: |  | 0 |  |  |  | Version: | 2.41
#DIV/0!
#DIV/0!
#DIV/0!
Note on G3: While IIAR 2 does not apply to non-ammonia refrigerants, the user may wish to evaluate IIAR 2 design criteria.

## Facility Information
Facility Information and Design Notes
Facility Name: |  | ß Enter facility name here
Street: |  | ß Enter facility address here
City, State
Zip Code
Country
Machinery Room Name: |  | ß Enter name of the machinery room here
Refrigerant Evaluated: |  | ß Use drop-down box to select refrigerant category to evaluate
Date of Evaluation: |  | ß Enter date of the evaluation here
Year of Installation or Modification: |  | ß Enter year of installation or last significant modification to MR or refrigeration system
Code or Standard in effect in the Year listed: | IIAR 2-2021 (2021-Present) | ß Use drop-down box to select code or standard to establish as design basis for evaluation
Prepared by: |  | ß Enter name of the engineer who prepared the ventilation design basis evaluation
Title: |  | ß Enter title of the engineer who prepared the ventilation design basis evaluation
Company Name: |  | ß Enter name of the company that prepared the ventilation design basis evaluation
Click here if you are unsure what code applies to your location.
Design Basis and Evaluation Summary:
ß Enter a narrative description of the ventilation system design basis here.
In the data/analysis worksheets that follow, the following color scheme is used to differentiate user-input data cells from calculated output data cells.
Input data | Output data
Version: | 2.41
Next (continue)
Codes and Standards in force in these date ranges
IIAR 2 (1992-1998)
IIAR 2 (1999-2009)
IIAR 2-2008 Addendum A (2010-2013)
IIAR 2-2014 (2014-2021)
IIAR 2-2021 (2021-Present)
IMC (2000-2011)
IMC (2012-Present)
ASHRAE 15 (1992-2000)
ASHRAE 15 (2001-Present)
UMC (1988-1993), Adopted by California
UMC & CMC (1994-Present)
CSA B52 (1995-1998)
CSA B52 (1999-Present)
Refrigerant in use
Ammonia
Other (non-ammonia)
Note on B23: In this cell, insert the design basis statement with sufficient detail to explain the installation and analysis being conducted. Here is an example design basis statement for a machinery room designed in accordance with the CSA B52-1999 mechanical code: The CSA B52-1999 Mechanical Refrigeration code is the current code in force at this location and the last significant change to this refrigeration system and/or the machinery room was 2010. Therefore the CSA B52-1999 code was chosen to evaluate the design basis of this machinery room ventilation system. The Ventilation Evaluation worksheet summarizes the findings of the Refrigeration Compressor Room. The evaluation indicates that the Intermittent Temperature Control and Emergency ventilation scfm rates are adequate. However, the Continuous Ventilation is undersized by 936 scfm. An evaluation should be undertaken to determine the best way to remediate this shortfall per the CSA B52-1999 code. The CSA B52-1999 code doesn't list any discharge velocity or non-sparking construction requirements. Therefore these requirements are for the most part marked N/A. While it's not required by the selected code, all except the Continuous EF's are primarily of aluminum construction, which is generally accepted to be a non-sparking material. Therefore, these exhaust fans have been listed as Non-Sparking Construction.
Note on B26: Boxes in this spreadsheet shaded in yellow are user-inputs.
Note on C26: Boxes in this spreadsheet shaded in pink are calculated or output values.

## Machinery Room Information
Machinery Room Installation and Weather Data
Facility Name: |  | 0 |  |  | Date: | 0
Room Name: |  | 0 |  |  | IIAR 2-2021 (2021-Present)
| Machinery Room Information: |  |  | Refrigerant Evaluated: |  | 0
Physical Dimensions:
| Specify input method for machinery room physical information |  |  |  |  | Volume
| Note: Cells with |  | formatting, are cells not used when certain selections are made throughout the spreadsheet.
|  | Input Data | North wall = |  | ft | 0 | m
|  |  | East wall = |  | ft | 0 | m
|  |  | South wall = |  | ft | 0 | m
|  |  | West wall = |  | ft | 0 | m
|  |  | Volume = |  | ft3 | 0 | m3
|  |  | Floor Area = |  | ft2 | 0 | m2
|  |  | Wall height = |  | ft | 0 | m
Design Notes:
|  | Output Data | Area = | 0 | ft2 | 0 | m2
|  |  | Volume = | 0 | ft3 | 0 | m3
Detector Information:
Detector installed that activates Ventilation & supervised alarm?
|  |  | Maximum detector setpoint allowed by code and/or standard = |  | ppm | 0 | ppm
|  |  | Setpoint activating Emergency Ventilation & supervised alarm = |  | ppm | 0 | ppm
MR Location and Occupancy Information:
Is Machinery Room in a basement?
|  |  | Design Occupancy = |  | persons | 0 | persons
| Refrigeration System Charge = |  |  |  | lb | 0 | kg
| Roof |  | Is this surface sunlit?
|  |  | Sunlit roof width = |  | ft | 0 | m
|  |  | Sunlit roof length = |  | ft | 0 | m
|  |  | Roof area sunlit = | 0 | ft2 | 0 | m2
|  |  | Roof U Factor = |  | Btu/hr-ft2-°F | 0 | WT/m2-°C
|  |  | Roof color = |  |  | 0
|  |  | Roof solar effects = | 0 | °F | 0 | °C
|  | Roof transmission load = |  | 0 | Btu/hr | 0 | WT
| North |  | Is this surface sunlit? | No
|  |  | North wall solar effects = | 0 | °F | 0 | °C
|  | North wall transmission load = |  | 0 | Btu/hr | 0 | WT
| East |  | Is this surface sunlit?
|  |  | Sunlit east wall length = |  | ft | 0 | m
|  |  | Sunlit east wall height = |  | ft | 0 | m
|  |  | East wall area sunlit = | 0 | ft2 | 0 | m2
| East |  | East wall U Factor = |  | Btu/hr-ft2-°F | 0 | WT/m2-°C
|  |  | East wall color = |  |  | 0
|  |  | East wall solar effects = | 0 | °F | 0 | °C
|  | East wall transmission load = |  | 0 | Btu/hr | 0 | WT
| South |  | Is this surface sunlit?
|  |  | Sunlit south wall length = |  | ft | 0 | m
|  |  | Sunlit south wall height = |  | ft | 0 | m
|  |  | South wall area sunlit = | 0 | ft2 | 0 | m2
| South |  | South Wall U Factor = |  | Btu/hr-ft2-°F | 0 | WT/m2-°C
|  |  | South Wall Color = |  |  | 0
|  |  | South Wall Solar Effects = | 0 | °F | 0 | °C
|  | South Wall Transmission Load = |  | 0 | Btu/hr | 0 | WT
| West |  | Is this surface sunlit?
|  |  | Sunlit west wall length = |  | ft | 0 | m
|  |  | Sunlit west wall height = |  | ft | 0 | m
|  |  | West wall area sunlit = | 0 | ft2 | 0 | m2
|  |  | West Wall U Factor = |  | Btu/hr-ft2-°F | 0 | WT/m2-°C
|  |  | West Wall Color = |  |  | 0
|  |  | West Wall Solar Effects = | 0 | °F | 0 | °C
|  | West Wall Transmission Load = |  | 0 | Btu/hr | 0 | WT
|  |  | Room Envelope Heat Load = | 0 | Btu/hr
|  |  | Machinery Room Motors= | 0
|  |  | Machinery Room Heat Inputs= | 0 | Btu/hr | 0 | kW
|  |  | Design Heat Load = | 0 | Btu/hr | 0 | kW
Weather Information:
|  |  | Design Outside Air: Toa,db |  | °F | -17.7778 | °C
|  |  | Design Supply Air Temp.: Tsa,db |  | °F | -17.7778 | °C
|  |  | Max Machinery Room Design Air Temp.: Tmr,db | 104 | °F | 40 | °C
Note - IIAR 2 requires the 1% design weather condition be used. The 1% condition is the dry bulb temperature exceeded 1% of the year (88 hrs). Design weather data is available in the ASHRAE Handbook of Fundamentals. The Handbook also includes 0.4% and 2% design conditions.
Prepared By: |  | 0 |  |  |  | Version: | 2.41
Next (continue)
| List for wall surface colors |  | Sunlight?
| Exterior Color |  | Yes
| Dark |  | No
Medium
Light
N/A
Method of input for physical data
Wall lengths
Volume
Floor area
Note on F13: If the machinery room has more than one roof height or irregular wall lengths, select "Volume" in the above drop down box and input the gross volume of the machinery room here, otherwise leave blank. Note, if the machinery room has directly connected "adjacent rooms" containing refrigeration machinery/equipment that will be included in this design, the volume input here should include the added volume of any adjacent room(s).
Note on F14: If "Floor Area", or "Volume" is selected in the above drop down box, input the gross floor area of the machinery room here otherwise leave blank. Note, if the machinery room has directly connected "adjacent rooms" containing refrigeration machinery/equipment that will be included in this design, the floor area input here should include the added area of any adjacent room(s).
Note on F15: If "Volume" is selected in the above drop down box, leave blank.
Note on F31: This represents the total charge of refrigerant in the largest system, any part of which is in the machinery room.
Note on F34: Input the width of the sunlit portion of the roof over the machinery room so that when multiplied by the "Sunlit length" will result in the total roof area that is sunlit.
Note on F35: Input the length of the sunlit portion of the roof over the machinery room so that when multiplied by the "Sunlit width" will result in the total roof area that is sunlit.
Note on E39: From 2006 ASHRAE Handbook - Refrigeration Chapter 13, Table 3 Allowance for Sun Effect
Note on F39: Reference: Table 4 in IIAR Bulletin 111-2002.
Note on F43: The North Wall is generally accepted to not have any solar exposure so the temperature effect is set to zero.
Note on F44: North-facing surfaces are generally accepted to not have any solar exposure.
Note on F80: Summer outdoor air design dry bulb temperature from ASHRAE Tables
Note on F81: Supply air temperature could be lowered by evaporative cooling or other mechanical means, etc. If not, the supply air temperature will be the same as the design outside air temperature.
Note on F82: Max Machinery Room Design Air Temp. is selected based on the code or standard selected.

## Machinery Room Motors
Machinery Room Electric Motors Installation
Facility Name: |  | 0 |  |  |  | Date: | 0
Room Name: |  | 0 |  |  | IIAR 2-2021 (2021-Present)
|  | Refrigerant Evaluated: |  |  | 0
| Equipment # |  | Operating (HP) | Operating h (% Eff) | Motor Load (Btu/hr) | Standby (HP) | Standby h (% Eff) | Motor Load (Btu/hr)
1 |  |  |  |  | 0 |  |  | 0
2 |  |  |  |  | 0 |  |  | 0
3 |  |  |  |  | 0 |  |  | 0
4 |  |  |  |  | 0 |  |  | 0
5 |  |  |  |  | 0 |  |  | 0
6 |  |  |  |  | 0 |  |  | 0
7 |  |  |  |  | 0 |  |  | 0
8 |  |  |  |  | 0 |  |  | 0
9 |  |  |  |  | 0 |  |  | 0
10 |  |  |  |  | 0 |  |  | 0
11 |  |  |  |  | 0 |  |  | 0
12 |  |  |  |  | 0 |  |  | 0
13 |  |  |  |  | 0 |  |  | 0
14 |  |  |  |  | 0 |  |  | 0
15 |  |  |  |  | 0 |  |  | 0
16 |  |  |  |  | 0 |  |  | 0
17 |  |  |  |  | 0 |  |  | 0
18 |  |  |  |  | 0 |  |  | 0
19 |  |  |  |  | 0 |  |  | 0
20 |  |  |  |  | 0 |  |  | 0
21 |  |  |  |  | 0 |  |  | 0
22 |  |  |  |  | 0 |  |  | 0
23 |  |  |  |  | 0 |  |  | 0
24 |  |  |  |  | 0 |  |  | 0
25 |  |  |  |  | 0 |  |  | 0
26 |  |  |  |  | 0 |  |  | 0
27 |  |  |  |  | 0 |  |  | 0
28 |  |  |  |  | 0 |  |  | 0
29 |  |  |  |  | 0 |  |  | 0
30 |  |  |  |  | 0 |  |  | 0
31 |  |  |  |  | 0 |  |  | 0
32 |  |  |  |  | 0 |  |  | 0
33 |  |  |  |  | 0 |  |  | 0
34 |  |  |  |  | 0 |  |  | 0
35 |  |  |  |  | 0 |  |  | 0
36 |  |  |  |  | 0 |  |  | 0
37 |  |  |  |  | 0 |  |  | 0
38 |  |  |  |  | 0 |  |  | 0
39 |  |  |  |  | 0 |  |  | 0
40 |  |  |  |  | 0 |  |  | 0
41 |  |  |  |  | 0 |  |  | 0
42 |  |  |  |  | 0 |  |  | 0
43 |  |  |  |  | 0 |  |  | 0
44 |  |  |  |  | 0 |  |  | 0
45 |  |  |  |  | 0 |  |  | 0
46 |  |  |  |  | 0 |  |  | 0
47 |  |  |  |  | 0 |  |  | 0
48 |  |  |  |  | 0 |  |  | 0
49 |  |  |  |  | 0 |  |  | 0
50 |  |  |  |  | 0 |  |  | 0
51 |  |  |  |  | 0 |  |  | 0
52 |  |  |  |  | 0 |  |  | 0
53 |  |  |  |  | 0 |  |  | 0
54 |  |  |  |  | 0 |  |  | 0
55 |  |  |  |  | 0 |  |  | 0
56 |  |  |  |  | 0 |  |  | 0
57 |  |  |  |  | 0 |  |  | 0
58 |  |  |  |  | 0 |  |  | 0
59 |  |  |  |  | 0 |  |  | 0
60 |  |  |  |  | 0 |  |  | 0
61 |  |  |  |  | 0 |  |  | 0
62 |  |  |  |  | 0 |  |  | 0
63 |  |  |  |  | 0 |  |  | 0
64 |  |  |  |  | 0 |  |  | 0
65 |  |  |  |  | 0 |  |  | 0
66 |  |  |  |  | 0 |  |  | 0
67 |  |  |  |  | 0 |  |  | 0
68 |  |  |  |  | 0 |  |  | 0
69 |  |  |  |  | 0 |  |  | 0
70 |  |  |  |  | 0 |  |  | 0
71 |  |  |  |  | 0 |  |  | 0
72 |  |  |  |  | 0 |  |  | 0
73 |  |  |  |  | 0 |  |  | 0
74 |  |  |  |  | 0 |  |  | 0
75 |  |  |  |  | 0 |  |  | 0
76 |  |  |  |  | 0 |  |  | 0
77 |  |  |  |  | 0 |  |  | 0
78 |  |  |  |  | 0 |  |  | 0
79 |  |  |  |  | 0 |  |  | 0
80 |  |  |  |  | 0 |  |  | 0
81 |  |  |  |  | 0 |  |  | 0
82 |  |  |  |  | 0 |  |  | 0
83 |  |  |  |  | 0 |  |  | 0
84 |  |  |  |  | 0 |  |  | 0
85 |  |  |  |  | 0 |  |  | 0
86 |  |  |  |  | 0 |  |  | 0
87 |  |  |  |  | 0 |  |  | 0
88 |  |  |  |  | 0 |  |  | 0
89 |  |  |  |  | 0 |  |  | 0
90 |  |  |  |  | 0 |  |  | 0
91 |  |  |  |  | 0 |  |  | 0
92 |  |  |  |  | 0 |  |  | 0
93 |  |  |  |  | 0 |  |  | 0
94 |  |  |  |  | 0 |  |  | 0
95 |  |  |  |  | 0 |  |  | 0
| TOTAL MOTORS |  | 0 |  | 0 | 0 |  | 0
Prepared By: |  | 0 |  |  |  |  | Version: | 2.41
Next (continue)
Note on G3: While IIAR 2 does not apply to non-ammonia refrigerants, the user may wish to evaluate IIAR 2 design criteria.
Note on C5: Hermetic refrigerant pumps are normally not included because the motor heat load goes into the refrigerant not to the machinery room space directly.
Note on F5: In this column, insert the electric motor efficiency (in percent) for each electric motor located in the machinery room.
Note on G5: This is a calculated machinery room internal heat load for each operating motor based on the input motor HP and electric motor efficiency specified.
Note on H5: Not included in calculations.
Note on I5: Not included in calculations.
Note on J5: Not included in calculations.

## Machinery Room Heat Inputs
Machinery Room Heat Inputs
Facility Name: |  | 0 |  | Date: | 0
Room Name: |  | 0 |  | IIAR 2-2021 (2021-Present)
|  | Refrigerant Evaluated: |  | 0
| Heat Generating Item |  | Heat Load (Btu/hr) | Notes
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
| TOTAL HEAT INPUTS |  | 0
Prepared By: |  | 0 |  |  | Version: | 2.41
Next (continue)
Note on H3: While IIAR 2 does not apply to non-ammonia refrigerants, the user may wish to evaluate IIAR 2 design criteria.
Note on C5: Name of the item adding heat to the machinery room. Example: Boiler, or Steam Generator, or gas fired HVAC Unit, etc.
Note on G5: Enter the amount of heat the item is adding to the space.

## Machinery Room Ventilation
Machinery Room Ventilation System Installation
| Facility Name: |  | 0 | [8 empty] | Date: | 0
| Room Name: |  | 0 |  |  | Refrigerant Evaluated: |  | 0 |  | IIAR 2-2021 (2021-Present)
| Exhaust Fan Information |  |  |  | List the exhaust fan CFM available for each mode of operation
[5 empty] | Normal (Temperature Control) Ventilation |  |  | Continuous (Occupant) Ventilation |  |  | Emergency Ventilation
| # | Exhaust Fan Name |  | Type (use drop down box) | Non-Sparking Construction? Not Required by this Standard. | Normal CFM | Discharge Up with Minimum 2500 FPM Velocity? Not Required by this Standard. | Non-Sparking Construction? Not Required by this Standard. | Continuous CFM | Discharge Up with Minimum 2500 FPM Velocity? Not Required by this Standard. | Non-Sparking Construction as Required by this Standard? | Emergency CFM | Discharge Up with Minimum 2500 FPM Velocity as Required by this Standard?
| 1 |  |  | - | - |  | - | - |  | - | - |  | -
| 2 |  |  | - | - |  | - | - |  | - | - |  | -
| 3 |  |  | - | - |  | - | - |  | - | - |  | -
| 4 |  |  | - | - |  | - | - |  | - | - |  | -
| 5 |  |  | - | - |  | - | - |  | - | - |  | -
| 6 |  |  | - | - |  | - | - |  | - | - |  | -
| 7 |  |  | - | - |  | - | - |  | - | - |  | -
| 8 |  |  | - | - |  | - | - |  | - | - |  | -
| 9 |  |  | - | - |  | - | - |  | - | - |  | -
| 10 |  |  | - | - |  | - | - |  | - | - |  | -
|  | Total Exhaust Fan Operation |  |  | Not Known | 0 | Not Known | Not Known | 0 | Not Known | Not Known | 0 | Not Known
| Supply Fan Information |  |  |  | List the supply fan CFM available for each mode of operation
[5 empty] | Normal (Temperature Control) Ventilation |  |  | Continuous (Occupant) Ventilation |  |  | Emergency Ventilation
| # | Supply Fan Name |  | Type | Normal CFM |  |  | Continuous CFM |  |  | Emergency CFM
| 1 |  |  | -
| 2 |  |  | -
| 3 |  |  | -
| 4 |  |  | -
| 5 |  |  | -
| 6 |  |  | -
| 7 |  |  | -
| 8 |  |  | -
| 9 |  |  | -
| 10 |  |  | -
|  | Total Supply Air Operation |  |  | 0 |  |  | 0 |  |  | 0
| Prepared By: |  | 0 | [8 empty] | Version: | 2.41
Next (continue)
|  | - | -
|  | Yes | Fixed Speed
|  | No | Variable Speed
N/A
Not Known
Note on K3: While IIAR 2 does not apply to non-ammonia refrigerants, the user may wish to evaluate IIAR 2 design criteria.
Note on F7: Non-Sparking Construction required by: -IIAR 2-2008 Addendum A 13.3.7.2, -IIAR 2-2014 6.14.3.6, 6.14.3.7 Use the dropdown box to select: -, Yes, No, N/A, or Not known.
Note on H7: Minimum 2500 FPM Discharge Velocity required by: -IIAR 2-2008 Addendum A 13.3.7.1, -IIAR 2-2014 6.14.3.5 Use the dropdown box to select: -, Yes, No, N/A, or Not known.
Note on I7: Non-Sparking Construction required by: -IIAR 2-2008 Addendum A 13.3.7.2, -IIAR 2-2014 6.14.3.6, 6.14.3.7 Use the dropdown box to select: -, Yes, No, N/A, or Not known.
Note on K7: Minimum 2500 FPM Discharge Velocity required by: -IIAR 2-2008 Addendum A 13.3.7.1, -IIAR 2-2014 6.14.3.5 Use the dropdown box to select: -, Yes, No, N/A, or Not known.
Note on L7: Non-Sparking Construction required by: -IIAR 2-2008 Addendum A 13.3.7.2, -IIAR 2-2014 6.14.3.6, 6.14.3.7 -IIAR 2-2021 6.14.3.5, 6.14.3.6 Use the dropdown box to select: -, Yes, No, N/A, or Not known.
Note on N7: Minimum 2500 FPM Discharge Velocity required by: -IIAR 2-2008 Addendum A 13.3.7.1, -IIAR 2-2014 6.14.3.5 -IIAR 2-2021 6.14.3.4 Use the dropdown box to select: -, Yes, No, N/A, or Not known.

## Machinery Room Summary
Machinery Room Ventilation Codes and Standards Summary
Facility Name: |  | 0 |  |  | Date: | 0
Refrigerant Evaluated: |  | 0 |  | IIAR 2-2021 (2021-Present)
Machinery Room Design and Installation Summary
For Room Name: |  | 0
| Machinery Room Area = |  |  | 0 | ft2 | 0 | m2
| Machinery Room Volume = |  |  | 0 | ft3 | 0 | m3
| Detector installed that activates Ventilation & supervised alarm? |  |  | 0 |  | 0
| Maximum detector setpoint allowed by code and/or standard = |  |  | 0 | ppm | 0 | ppm
| Setpoint activating Emergency Ventilation & supervised alarm = |  |  | 0 | ppm | 0 | ppm
| Is Machinery Room in a basement? |  |  | 0 |  | 0
| Design Occupancy = |  |  | 0 | persons | 0 | persons
| Installed Refrigerant system charge (largest system) = |  |  | 0 | lb | 0 | kg
| Installed total Machinery Room motor HP = |  |  | 0 | HP | 0 | kW
| Installed Machinery Room motor heat load = |  |  | 0 | Btu/hr | 0 | kW
| Installed Machinery Room envelope heat load = |  |  | 0 | Btu/hr | 0 | kW
| Machinery Room Heat Inputs = |  |  | 0 | Btu/hr | 0 | kW
| Installed Total Machinery Room design heat load = |  |  | 0 | Btu/hr | 0 | kW
Ventilation Summary:
Exhaust Fans:
| Installed Total Normal (Temperature Control) Ventilation CFM = |  |  | 0 | ft3 / min | 0 | l/s
| Installed Total Continuous (Occupant) CFM = |  |  | 0 | ft3 / min | 0 | l/s
| Installed Total Emergency CFM = |  |  | 0 | ft3 / min | 0 | l/s
Supply Air:
| Installed Total Normal (Temperature Control) Ventilation CFM = |  |  | 0 | ft3 / min | 0 | l/s
| Installed Total Continuous (Occupant) CFM = |  |  | 0 | ft3 / min | 0 | l/s
| Installed Total Emergency CFM = |  |  | 0 | ft3 / min | 0 | l/s
Codes and Standards Ventilation Rate Requirements
IIAR 2 (1992-1998)
Normal (Temperature Control) Ventilation Requirement:
| Normal Ventilation: |  | (18°F temp rise) | 0 | ft3 / min | 0 | l/s
| Design Basis Normal: |  | (18°F temp rise) | 0 | ft3 / min | 0 | l/s
Continuous Ventilation Requirement:
| Continuous (Occupant) Ventilation: |  | (NO detector and/or setpoint > max) | 0 | ft3 / min | 0 | l/s
|  |  | (When machinery room is in a basement) | 0 | ft3 / min | 0 | l/s
|  |  | (0.5 CFM/ft2) | 0 | ft3 / min | 0 | l/s
| Design Basis Continuous: |  | (NO detector and/or setpoint > max) | 0 | ft3 / min | 0 | l/s
Emergency Ventilation Requirement:
| Emergency Ventilation: |  | (Refrigerant quantity) | 0
| Design Basis Emergency: |  | (Refrigerant quantity) | 0 | ft3 / min | 0 | l/s
IIAR 2 (1999-2009)
Normal (Temperature Control) Ventilation Requirement:
| Normal Ventilation: |  | (18°F temp rise) | 0 | ft3 / min | 0 | l/s
| Design Basis Normal: |  | (18°F temp rise) | 0 | ft3 / min | 0 | l/s
Continuous Ventilation Requirement:
| Continuous (Occupant) Ventilation: |  | (NO detector and/or setpoint > max) | 0 | ft3 / min | 0 | l/s
|  |  | (When machinery room is in a basement) | 0 | ft3 / min | 0 | l/s
|  |  | (0.5 CFM/ft2) | 0 | ft3 / min | 0 | l/s
| Design Basis Continuous: |  | (NO detector and/or setpoint > max) | 0 | ft3 / min | 0 | l/s
Emergency Ventilation Requirement (larger of):
| Emergency Ventilation: |  | (Refrigerant quantity) | 0 | ft3 / min | 0 | l/s
-or-
|  |  | (Room volume * 0.2) | 0 | ft3 / min | 0 | l/s
| Design Basis Emergency: |  | (Refrigerant quantity) | 0 | ft3 / min | 0 | l/s
IIAR 2-2008 Addendum A (2010-2013)
Normal (Temperature Control) Ventilation Requirement:
| Normal Ventilation: |  | (104°F max temp) | 0 | ft3 / min | 0 | l/s
-or-
|  |  | (20 ACH) | 0 | ft3 / min | 0 | l/s
| Design Basis Normal: |  | (104°F max temp) | 0 | ft3 / min | 0 | l/s
Continuous Ventilation Requirement:
| Continuous (Occupant) Ventilation: |  | N/A | 0 | ft3 / min | 0 | l/s
|  |  | (NO detector and/or setpoint > max) | 0 | ft3 / min | 0 | l/s
| Design Basis Continuous: |  | N/A | 0 | ft3 / min | 0 | l/s
Emergency Ventilation Requirement:
| Design Basis Emergency: |  | (1 Fan Failure & 20 ACH) | 0 | ft3 / min | 0 | l/s
|  |  | (30 ACH) | 0 | ft3 / min | 0 | l/s
IIAR 2-2014 (2014-2021)
Normal (Temperature Control) Ventilation Requirement:
| Normal Ventilation: |  | (104°F max temp) | 0 | ft3 / min | 0 | l/s
| Design Basis Normal: |  | (104°F max temp) | 0 | ft3 / min | 0 | l/s
Continuous Ventilation Requirement:
| Continuous (Occupant) Ventilation: |  | (20 CFM/person when occupied) | 0 | ft3 / min | 0 | l/s
- or -
|  |  | (0.5 CFM/ft2 when occupied) | 0 | ft3 / min | 0 | l/s
|  |  | (NO detector and/or setpoint > max) | 0 | ft3 / min | 0 | l/s
| Design Basis Continuous: |  | (20 CFM/person when occupied) | 0 | ft3 / min | 0 | l/s
Emergency Ventilation Requirement:
| Design Basis Emergency: |  | N/A | 0
|  |  | (30 ACH) | 0 | ft3 / min | 0 | l/s
IIAR 2-2021 (2021-Present)
Normal (Temperature Control) Ventilation Requirement:
| Normal Ventilation: |  | (104°F max temp) | 0 | ft3 / min | 0 | l/s
| Design Basis Normal: |  | (104°F max temp) | 0 | ft3 / min | 0 | l/s
Ventilation for Occupants Requirement:
| Continuous (Occupant) Ventilation: |  | (20 CFM/person when occupied) | 0 | ft3 / min | 0 | l/s
- or -
|  |  | (0.5 CFM/ft2 when occupied) | 0 | ft3 / min | 0 | l/s
|  |  | (NO detector and/or setpoint > max) | 0 | ft3 / min | 0 | l/s
| Design Basis Continuous: |  | (20 CFM/person when occupied) | 0 | ft3 / min | 0 | l/s
Emergency Ventilation Requirement:
| Design Basis Emergency: |  | N/A | 0
|  |  | (30 ACH) | 0 | ft3 / min | 0 | l/s
IMC (2000-2011)
Normal (Temperature Control) Ventilation Requirement:
| Normal Ventilation: |  | (Max 18°F temp rise when occupied) | 0 | ft3 / min | 0 | l/s
| Design Basis Normal: |  | (Max 18°F temp rise when occupied) | 0 | ft3 / min | 0 | l/s
Normal Continuous Ventilation Requirement (larger of):
| Continuous (Occupant) Ventilation: |  | (NO detector and/or setpoint > max) | 0 | ft3 / min | 0 | l/s
|  |  | (20 CFM/person when occupied) | 0 | ft3 / min | 0 | l/s
- or -
|  |  | (0.5 CFM/ft2 when occupied) | 0 | ft3 / min | 0 | l/s
| Design Basis Continuous: |  | (NO detector and/or setpoint > max) | 0 | ft3 / min | 0 | l/s
Emergency Ventilation Requirement:
| Emergency Ventilation: |  | (Refrigerant quantity) | 0 | ft3 / min
| Design Basis Emergency: |  | (Refrigerant quantity) | 0 | ft3 / min | 0 | l/s
IMC (2012-Present)
Normal (Temperature Control) Ventilation Requirement:
| Normal Ventilation: |  | (Max 18°F temp rise when occupied) | 0 | ft3 / min | 0 | l/s
| Design Basis Normal: |  | (Max 18°F temp rise when occupied) | 0 | ft3 / min | 0 | l/s
Normal Continuous Ventilation Requirement (larger of):
| Continuous (Occupant) Ventilation: |  | (NO detector and/or setpoint > max) | 0 | ft3 / min | 0 | l/s
- or -
|  |  | (20 CFM/person when occupied) | 0 | ft3 / min | 0 | l/s
- or -
|  |  | (0.5 CFM/ft2 when occupied) | 0 | ft3 / min | 0 | l/s
| Design Basis Continuous: |  | (NO detector and/or setpoint > max) | 0 | ft3 / min | 0 | l/s
Emergency Ventilation Requirement:
| Emergency Ventilation: |  | (Non-ammonia refrigerant qty) | 0 | ft3 / min | 0 | l/s
|  |  | (Ammonia 30 ACH) | 0 | ft3 / min | 0 | l/s
| Design Basis Emergency: |  | (Non-ammonia refrigerant qty) | 0 | ft3 / min | 0 | l/s
ASHRAE 15 (1992-2000)
Normal (Temperature Control) Ventilation Requirement:
| Normal Ventilation: |  | (Max 18°F temp rise when occupied) | 0 | ft3 / min | 0 | l/s
| Design Basis Normal: |  | (Max 18°F temp rise when occupied) | 0 | ft3 / min | 0 | l/s
Continuous Ventilation Requirement:
| Continuous (Occupant) Ventilation: |  | (NO detector and/or setpoint > max) | 0 | ft3 / min | 0 | l/s
- or -
|  |  | (20 CFM/person when occupied) | 0 | ft3 / min | 0 | l/s
- or -
|  |  | (0.5 CFM/ft2 when occupied) | 0 | ft3 / min | 0 | l/s
| Design Basis Continuous: |  | (NO detector and/or setpoint > max) | 0 | ft3 / min | 0 | l/s
Emergency Ventilation Requirement:
| Emergency Ventilation: |  | (Refrigerant quantity) | 0
| Design Basis Emergency: |  | (Refrigerant quantity) | 0 | ft3 / min | 0 | l/s
ASHRAE 15 (2001-Present)
Normal (Temperature Control) Ventilation Requirement:
| Normal Ventilation: |  | (Max 18°F temp rise when occupied) | 0 | ft3 / min | 0 | l/s
- or -
|  |  | (122°F max) | 0 | ft3 / min | 0 | l/s
| Design Basis Normal: |  | (Max 18°F temp rise when occupied) | 0 | ft3 / min | 0 | l/s
Continuous Ventilation Requirement:
| Continuous (Occupant) Ventilation: |  | (NO detector and/or setpoint > max) | 0 | ft3 / min | 0 | l/s
- or -
|  |  | (20 CFM/person when occupied) | 0 | ft3 / min | 0 | l/s
- or -
|  |  | (0.5 CFM/ft2 when occupied) | 0 | ft3 / min | 0 | l/s
| Design Basis Continuous: |  | (NO detector and/or setpoint > max) | 0 | ft3 / min | 0 | l/s
Emergency Ventilation Requirement:
| Emergency Ventilation: |  | (Refrigerant quantity) | 0
| Design Basis Emergency: |  | (Refrigerant quantity) | 0 | ft3 / min | 0 | l/s
UMC (1988-1993), Adopted by California
Emergency Ventilation Requirement:
| Emergency Ventilation: |  | (12 ACH) | 0 | ft3 / min | 0 | l/s
| Design Basis Emergency: |  | (12 ACH) | 0 | ft3 / min | 0 | l/s
UMC & CMC (1994-Present)
Normal (Temperature Control) Ventilation Requirement:
| Normal Ventilation: |  | (104°F max temp) | 0 | ft3 / min | 0 | l/s
| Design Basis Normal: |  | (104°F max temp) | 0 | ft3 / min | 0 | l/s
Continuous Ventilation Requirement:
| Continuous (Occupant) Ventilation: |  | (NO detector and/or setpoint > max) | 0 | ft3 / min | 0 | l/s
- or -
|  |  | (0.5 CFM/ft2) | 0 | ft3 / min | 0 | l/s
- or -
|  |  | (Maintaining negative 0.05" H2O) | 0
| Design Basis Continuous: |  | (NO detector and/or setpoint > max) | 0 | ft3 / min | 0 | l/s
Emergency Ventilation Requirement:
| Emergency Ventilation: |  | (Refrigerant quantity) | 0
| Design Basis Emergency: |  | (Refrigerant quantity) | 0 | ft3 / min | 0 | l/s
CSA B52 (1995-1998)
Normal (Temperature Control) Ventilation Requirement:
| Normal Ventilation: |  | (18°F Temp rise in operation/occupied) | 0 | ft3 / min | 0 | l/s
| Design Basis Normal: |  | (18°F Temp rise in operation/occupied) | 0 | ft3 / min | 0 | l/s
Continuous Ventilation Requirement:
| Continuous (Occupant) Ventilation: |  | (NO detector and/or setpoint > max) | 0 | ft3 / min | 0 | l/s
- or -
|  |  | (Machinery Room in a Basement) | 0 | ft3 / min | 0 | l/s
- or -
|  |  | (0.5 CFM/ft2 in operation/occupied) | 0 | ft3 / min | 0 | l/s
| Design Basis Continuous: |  | (NO detector and/or setpoint > max) | 0 | ft3 / min | 0 | l/s
Emergency Ventilation Requirement:
| Emergency Ventilation: |  | (Refrigerant Qty <= 15,400 lbs) | 0 | ft3 / min | 0 | l/s
- or -
|  |  | (Refrigerant Qty > 15,400 lbs) | 0 | ft3 / min | 0 | l/s
| Design Basis Emergency: |  | (Refrigerant Qty <= 15,400 lbs) | 0 | ft3 / min | 0 | l/s
CSA B52 (1999-Present)
Normal (Temperature Control) Ventilation Requirement:
| Normal Ventilation: |  | (18°F Temp rise in operation/occupied) | 0 | ft3 / min | 0 | l/s
| Design Basis Normal: |  | (18°F Temp rise in operation/occupied) | 0 | ft3 / min | 0 | l/s
Continuous Ventilation Requirement:
| Continuous (Occupant) Ventilation: |  | (NO detector and/or setpoint > max) | 0 | ft3 / min | 0 | l/s
- or -
|  |  | (Machinery Room in a Basement) | 0 | ft3 / min | 0 | l/s
- or -
|  |  | (0.5 CFM/ft2 in operation/occupied) | 0 | ft3 / min | 0 | l/s
| Design Basis Continuous: |  | (NO detector and/or setpoint > max) | 0 | ft3 / min | 0 | l/s
Emergency Ventilation Requirement:
| Emergency Ventilation: |  | (Refrigerant Qty <= 15,400 lbs) | 0 | ft3 / min | 0 | l/s
- or -
|  |  | (Refrigerant Qty > 15,400 lbs) | 0 | ft3 / min | 0 | l/s
| Design Basis Emergency: |  | (Refrigerant Qty <= 15,400 lbs) | 0 | ft3 / min | 0 | l/s
Prepared By: |  | 0 |  |  |  | Version: | 2.41
Next (continue)
Note on F3: While IIAR 2 does not apply to non-ammonia refrigerants, the user may wish to evaluate IIAR 2 design criteria.

## IIAR 2-1992
IIAR 2 (1992-1998)
We would like to acknowledge and thank the International Institute of Ammonia Refrigeration (IIAR) for granting permission to include the following excerpts from its Standard 2.
Summary of Key Ventilation Provisions
4.3 | Ventilation
4.3.1
In order to be considered a “Non-Hazardous (Unclassified) Location”, in accordance with the National Electric Code (see 6.9) the machinery room shall be provided with an independent mechanical ventilation system (see 6.5) operated according to one of the alternates described in paragraph 4.3.2 or 4.3.3. Where a mechanical ventilation system is not provided in accordance with this standard, the room shall be considered a Class I, Group D, Division 2 location. All electrical equipment in the room shall conform to the requirements for a Class I, Group D, Division 2 location, per the latest edition of the National Electric Code (see 6.9).
4.3.2
When provided with a continuously operated, independent mechanical ventilation system, the ventilation rate shall be the larger of the two rates described in paragraph 4.3.3.1.
4.3.3
The room may be provided with an independent mechanical ventilation system actuated automatically by vapor detector(s) and also operable manually. The typical recommended actuation level of the detection device is a setting less than 400 ppm. Where multiple alarm levels are desired, it is suggested that a setting below 1500 ppm be employed to avoid the point at which humans could be seriously affected. Further, to avoid potentially flammable situations, and where there exist no possible human affects, a setting below 40,000 ppm is suggested. 40,000 ppm represents approximately 25% of the level of the lower limit of flammability. The design ventilation rate shall be the larger of the two rates described in paragraph 4.3.3.1.
4.3.3.1
The mechanical ventilation required to exhaust a potential accumulation of refrigerant due to leaks or a rupture of the system shall be capable of removing air from the machinery room in the following minimum quantity: Q = 100 x G0.5 (cfm) [Q = 70 x G0.5 (I/s)] Where, Q = airflow in cubic feet per minute (litres per second) G = is the mass of refrigerant in pounds (kilograms) in the largest system, any part of which is located in the machinery room. A sufficient part of the mechanical ventilation shall be operated to provide normal volumes equal to the larger of the following: a) 0.5 cfm per square foot (2.54 I/s per square meter) of machinery room area. b) A volume required to maintain a maximum temperature rise above ambient of 18°F (10°C), based on all of the heat-producing machinery in the room.
4.3.3.2
To obtain the reduced air flow for normal ventilation, partial operation of a multiple fan system or multi-speed fans may be used, controlled by a thermostat and/or an ammonia detector.
4.3.4
In basements, the ventilation system shall be operated continuously at the larger of the ventilation rates described in 4.3.3.1.
4.3.5
A supervised alarm system shall be activated when the ammonia leak detector is activated or when the mechanical ventilation system fails so that corrective action can be taken. Periodic tests of the detectors, alarm system and mechanical ventilation system shall be performed, as recommended by the manufacturer.

## IIAR 2-1999
IIAR 2 (1999-2009)
We would like to acknowledge and thank the International Institute of Ammonia Refrigeration (IIAR) for granting permission to include the following excerpts from its Standard 2.
Summary of Key Ventilation Provisions
6.2 | Ventilation
6.2.1.1
In order to be considered a "Non-Hazardous (Unclassified) Location,” in accordance with the National Electric Code (8.9), the machinery room shall be provided with an independent mechanical ventilation system (8.5) operated according to either 6.2.3.1 or 6.2.3.2.
6.2.1.2
Where a mechanical ventilation system is not provided in accordance with this standard, the room shall be considered a Class 1, Group D, Division 2, location. All electrical equipment in the room shall conform to the requirements for a Class 1, Group D, Division 2 location, per the governing edition of the National Electric Code (8.9).
6.2.1.3
A supervised alarm system shall be activated when the ammonia leak detector is activated or when the mechanical ventilation system fails so that corrective action can be taken.
6.2.3.1
The machinery room shall be provided with an independent mechanical ventilation system actuated automatically by vapor detector(s) and also operable manually.
6.2.3.1.1
The typical recommended actuation level of the detection device is a setting less than 400 ppm; however, activation levels shall be set as required by the jurisdictional authority.
6.2.3.1.2
Where one or more alarm levels are used, the level actuating the ventilation system shall not exceed 1000 ppm.
6.2.3.2
When continuously operated (without automatic actuation), the mechanical ventilation shall be at the emergency ventilation rate as specified in paragraph 6.2.3.3.
6.2.3.3
The emergency mechanical ventilation rate shall be the larger of the following two rates:
6.2.3.3.1
Q = 100*G0.5 (ft3 ⁄ min) [Q = 0.70*G0.5 (m3 ⁄ s )] Where, Q = airflow in ft3/min (m3/s) G = the mass of refrigerant in lb (kg) in the largest system, any part of which is located in the machinery room.
6.2.3.3.2
Q = V × 0.2 (ft3 ⁄ min) [Q = V x 0.003 (m3 / s)] Where, Q = airflow in ft3/min (m3/s) V = room volume in ft3 (m3)
6.2.3.4
A normal (non-emergency) ventilation rate shall be operated to provide normal ventilation volumes equal to the larger of the following:
6.2.3.4.1
0.5 ft3/min per ft2 (0.003 m3/s per m2) of machinery room area.
6.2.3.4.2
A volume required to maintain a maximum temperature rise above ambient of 18°F (10°C), based on all the heat producing machinery in the room.
6.2.3.5
To obtain the reduced airflow for normal ventilation, partial operation of a multiple fan system or multi-speed fans may be controlled manually or by a thermostat and/or an ammonia detector.
6.2.3.6
In basements, the ventilation system shall be operated continuously at the emergency ventilation rate in 6.2.3.3.

## IIAR 2-2008
IIAR 2 (1999-2009)
We would like to acknowledge and thank the International Institute of Ammonia Refrigeration (IIAR) for granting permission to include the following excerpts from its Standard 2.
Summary of Key Ventilation Provisions
13.1 | Room Layout
13.1.1.2
All machinery rooms shall be equipped with at least one ammonia detector connected to a supervised alarm.
13.2 | Ventilation
13.2.1.1
In order to be considered a “Non-Hazardous (Unclassified) Location,” in accordance with the National Electric Code [ref.4.1.5], the machinery room shall be provided with an independent mechanical ventilation system operated according to either 13.2.3.1 or 13.2.3.2.
13.2.1.2
Where a mechanical ventilation system is not provided in accordance with this standard, the room shall be considered a Class 1, Group D, Division 2, location. All electrical equipment in the room shall conform to the requirements for a Class 1, Group D, Division 2 location, per the governing edition of the National Electric Code [ref.4.1.5].
13.2.1.3
A supervised alarm system shall be activated when the ammonia leak detector is activated or when the mechanical ventilation system fails so that corrective action can be taken.
13.2.3.1
The machinery room shall be provided with an independent mechanical ventilation system actuated automatically by vapor detector(s) and also operable manually.
13.2.3.1.1
The typical recommended actuation level of the detection device is a setting less than 400 ppm; however, activation levels shall be set as required by the jurisdictional authority.
13.2.3.1.2
Where one or more alarm levels are used, the level actuating the ventilation system shall not exceed 1000 ppm.
13.2.3.2
When continuously operated (without automatic actuation), the mechanical ventilation shall be at the emergency ventilation rate as specified in paragraph 13.2.3.3.
13.2.3.3
The emergency mechanical ventilation rate shall be the larger of the following two rates: Q = 100*G0.5 (ft3 ⁄ min) [Q = 0.70*G0.5 (m3 ⁄ s )] Where, Q = airflow in ft3/min (m3/s) G = the mass of refrigerant in lb (kg) in the largest system, any part of which is located in the machinery room. Q = V × 0.2 (ft3 ⁄ min) [Q = V x 0.003 (m3 / s)] Where, Q = airflow in ft3/min (m3/s) V = room volume in ft3 (m3)
13.2.3.4
A normal (non-emergency) ventilation rate shall be operated to provide normal ventilation volumes equal to the larger of the following: a. 0.5 ft3/min per ft2 (0.003 m3/s per m2) of machinery room area. b. A volume required to maintain a maximum temperature rise above ambient of 18°F (10°C), based on all the heat producing machinery in the room.
13.2.3.5
To obtain the reduced airflow for normal ventilation, partial operation of a multiple fan system or multi-speed fans may be controlled manually or by a thermostat and/or an ammonia detector.
13.2.3.6
In basements, the ventilation system shall be operated continuously at the emergency ventilation rate in 13.2.3.3.

## IIAR 2-2008 Addendum A {2010}
IIAR 2-2008 Addendum A (2010-2013)
We would like to acknowledge and thank the International Institute of Ammonia Refrigeration (IIAR) for granting permission to include the following excerpts from its Standard 2.
Summary of Key Ventilation Provisions
13.2 | Refrigerant Detection
Each refrigerating machinery room shall contain at least two refrigerant detectors that actuate an alarm and mechanical ventilation.
13.2.1 Alarm
13.2.1.1
A monitored location shall be notified when the ammonia leak detector is activated so that corrective action can be taken. NOTE: “Monitored” is defined as a means of continual oversight such as pagers, on-site staff, third party alarm service or a responsible party.
13.2.1.2
The detectors shall activate visual and audible alarms inside the refrigerating machinery room and outside each entrance to the refrigerating machinery room.
13.2.3.1
One detector shall be utilized to activate an alarm and actuate the normal mechanical ventilation system (at its maximum design capacity) at a value not greater than the corresponding TLV-TWA.
13.2.3.2
The second detector shall be utilized to activate an alarm and actuate the emergency mechanical ventilation system at a level not exceeding 1000 ppm. Note: Additional ammonia detectors can be utilized to monitor refrigerant levels exceeding the range of the detectors in 13.2.3.1 and 13.2.3.2.
13.3 | Ventilation
13.3.1
Each refrigerating machinery room shall be vented to the outdoors by means of mechanical ventilation systems actuated automatically by refrigerant detector(s), temperature sensors, and also operable manually. The mechanical ventilation systems shall be designed to produce a normal ventilation rate as required by Section 13.3.8, and an emergency ventilation rate as required by section 13.3.9. The mechanical ventilation systems shall be powered independently of the machine room machinery, and shall not be subject to emergency shutdown controls.
13.3.2
Multiple fans or multispeed fans are allowed in order to produce the emergency ventilation rate and to obtain a reduced airflow for normal ventilation. (See Section 13.3.8) Ventilation fans shall be selected such that the failure of any single fan does not diminish the total ventilation rate to less than 20 Air Changes per Hour (ACH). Fans that are used for normal ventilation and which are also used for emergency ventilation must be controlled such that the emergency rate is achieved when required, regardless of room temperature.
13.3.3
Provision shall be made for inlet air to replace that being exhausted. Inlet air makeup shall be designed to provide a negative pressure in the machinery room with a maximum negative pressure of 0.25 in. water column.
13.3.7.1
All exhaust fans shall discharge up vertically with a minimum discharge velocity of 2500 FPM.
13.3.7.2
All exhaust fans shall be equipped with non-sparking blades.
13.3.8
Normal Mechanical Ventilation
13.3.8.1
Normal mechanical ventilation design capacity shall be the greater of: a. 20 Air Changes per hour (20 ACH) based on the total gross volume of the machinery room. b. The volume required to limit the room temperature to 104°F (40°C) taking into account the ambient heating effect of all machinery in the room and with the ventilation air entering the room at a 1% ASHRAE design. In the areas where ambient conditions could exceed 99°F, the emergency ventilation system is permitted to be used to supplement the normal ventilation during extreme conditions. EXCEPTION: A reduced normal ventilation rate can be used on applications where a means of cooling is provided or room electrical equipment is designed to accommodate temperatures exceeding 104°F (40°C), in accordance with UL and NEC standards.
13.3.8.2
To obtain the reduced airflow to maintain space temperatures for normal ventilation, partial operation of a multiple fan system or multi-speed fans can be utilized.
13.3.8.3
Normal ventilation need not be continuous and shall be actuated by: a. Space temperature (thermostat). b. A refrigerant detector at a value not greater than the corresponding TLV-TWA. c. Manual controls.
13.3.9
Emergency Mechanical Ventilation
13.3.9.1
Emergency mechanical ventilation systems shall be capable of providing at least one air change every two minutes, which is 30 air changes per hour (30 ACH) based on the gross machinery room volume.
13.3.9.2
Emergency mechanical ventilation shall be actuated by a. A refrigerant detector at a level not exceeding 1000 ppm. b. Manual controls

## IIAR 2-2014
IIAR 2-2014 (2014-2021)
We would like to acknowledge and thank the International Institute of Ammonia Refrigeration (IIAR) for granting permission to include the following excerpts from its Standard 2.
Summary of Key Ventilation Provisions
Chapter 5. General System Design Requirements
5.3 *Volume Calculation for Determining Concentration of an Ammonia Release.
For the purpose of applying Section 4.2.4 and Section 7.3.1.2, the volume used to calculate the potential ammonia concentration in the event of a release shall comply with this section. The volume used to calculate the potential ammonia concentration shall be the gross volume of a room or space into which released ammonia disperses based on the smallest gross volume in which the release will accumulate.
5.3.1 *Wall Openings.
Where spaces adjacent to those containing refrigeration systems, equipment, or portions thereof are connected by permanent wall openings, the volume of such adjacent spaces shall not contribute to the calculated volume used for ammonia release concentration calculations unless, based on the size and elevation of permanent wall openings or a mechanical ventilation system, the designer determines that migration and dilution of a release over the combined spaces will occur. The volume shall be the combined space, provided that the openings or mechanical ventilation are clearly identified as the basis for the design analysis.
5.3.2 Spaces Above Suspended Ceilings.
The space above a suspended ceiling shall not be included in the volume calculation unless the space above the ceiling functions as part of the air distribution system.
5.3.3 *Interconnected Floor Levels and Mezzanines.
Where a refrigeration system, or portion thereof, is located in a room or space containing multiple floor levels connected through an open atrium or where a mezzanine is open to a room or space, the combined volume of interconnected floors and mezzanines is permitted in the volume calculation.
5.3.4 *Mechanical Ventilation Considerations.
Where a refrigeration system, or portion thereof, is located 1) in an area served by a mechanical ventilation system that also serves additional spaces, 2) within an air handler, or 3) in an air distribution duct system, the volume of the rooms or spaces connected by the ventilation or duct system, including the volume of the connected supply and return air ducts exterior to the room and any connecting plenum, shall be used. EXCEPTION: The smaller of the volumes on either side of a damper shall be used where portions of the ventilation or duct system are subject to isolation by dampers, other than 1) fire dampers, 2) smoke dampers, 3) combination fire and smoke dampers, or 4) dampers that continuously maintain not less than 10% airflow.
Chapter 6. Machinery Rooms
6.5 Open Flames and Hot Surfaces.
Fuel-burning appliances and equipment and surfaces with temperatures exceeding 800°F (427°C) shall not be installed in a machinery room. EXCEPTIONS: 1. Fuel-burning appliances and equipment shall be permitted in a machinery room where combustion air to the fuel-burning appliance is ducted from outside of the machinery room and sealed to prevent ammonia leakage from reaching the combustion chamber. 2. Fuel-burning appliances and equipment shall be permitted in a machinery room where an ammonia detector is in accordance with Section 6.13 and automatically shuts off the combustion process upon detection of ammonia. 3. The use of matches, lighters, sulfur sticks, welding equipment, and similar portable devices shall be permitted except when charging is being performed and when oil or ammonia is being removed from the system. 4. Internal combustion engines powering compressors shall be permitted in a machinery room.
6.8 Electrical Safety
6.8.2 Hazardous (Classified) Locations.
Machinery rooms shall be designated Ordinary Locations, as described in the Electrical Code, where the machinery room is provided with emergency ventilation in accordance with Section 6.14.7 and ammonia detection in accordance with Section 6.13. Machinery rooms not provided with emergency ventilation shall be designated as not less than a Class I, Division 2, Group D Hazardous (Classified) Location, and electrical equipment installed in the machinery room shall be designed to meet this requirement.
6.12 *Emergency Control Switches
6.12.2 Emergency Ventilation Control Switch.
A clearly identified control switch for emergency ventilation with a tamper-resistant cover shall be located outside the machinery room and adjacent to the designated principal machinery room door. The switch shall provide “ON/AUTO” override capability for emergency ventilation. The function of the switch shall be clearly marked by signage near the controls.
6.13 Ammonia Detection and Alarm
6.13.1 General.
Machinery rooms shall be provided with ammonia detection and alarm in accordance with Sections 17.2–17.6 and the following features: 1. At least one ammonia detector shall be provided in the room or area. 2. The detector shall activate an alarm that reports to a monitored location so that corrective action can be taken at an indicated concentration of 25 ppm or higher. 3. Audible and visual alarms shall be provided inside the room to warn that access to the room is restricted to authorized personnel and emergency responders when the alarm has activated. Additional audible and visual alarms shall be located outside of each entrance to the machinery room.
6.13.2 Alarm Response
6.13.2.1
Detection of ammonia concentrations less than 25 ppm requires no alarm.
6.13.2.2
*Detection of ammonia concentrations equal to or exceeding 25 ppm shall activate visual indicators and audible alarms as specified in Section 6.13.1. The visual indicator and audible alarm shall be permitted to automatically reset if the ammonia concentration drops below 25 ppm.
6.13.2.3
*Detection of ammonia concentrations equal to or exceeding 150 ppm (1/2 IDLH) shall activate visual indicators and an audible alarm and shall activate emergency ventilation, where required, in accordance with Section 6.14.7. Once activated, emergency ventilation shall continue to operate until manually reset by a switch located in the machinery room.
6.13.2.4
*Detection of ammonia concentrations that exceed a detector’s upper detection limit or 40,000 ppm (25% LFL), whichever is lower, shall activate visual indicators and an audible alarm and shall activate emergency ventilation, where required, in accordance with Section 6.14.7. Once activated, emergency ventilation shall continue to operate until manually reset by a switch located in the machinery room. In addition, the following equipment in the machinery room shall be automatically de-energized: 1. Refrigerant compressors. 2. Refrigerant pumps. 3. Normally closed automatic refrigerant valves that are not part of an emergency control system.
6.14 | Ventilation
6.14.1 *Ventilation for Occupants.
In occupied conditions, outdoor air shall be provided at a rate of not less than 0.5 cfm/ft2 (0.0025 m3/s • m2) of machinery room area or 20 cfm (0.009 m3/s) per occupant, whichever is greater.
6.14.2 General Exhaust and Air Conditioning Equipment.
Machinery room exhaust fans and air conditioning equipment that is not intended for exhausting ammonia vapor shall be de-energized, and fan dampers, where provided, shall close upon detection of ammonia in accordance with Section 6.13.2.2.
6.14.3 Exhaust Ventilation.
Machinery rooms shall be vented to the outdoors by means of a mechanical exhaust ventilation system.
6.14.3.1
Mechanical exhaust ventilation systems shall be automatically activated by ammonia leak detection in accordance with Section 6.13 or temperature sensors and shall be manually operable.
6.14.3.2
Mechanical exhaust ventilation systems shall be designed to produce not less than the temperature control ventilation rate required by Section 6.14.6 and the emergency exhaust ventilation rate required by Section 6.14.7.
6.14.3.3
Exhaust air ducts from the machinery room shall serve only the machinery room.
6.14.3.4
*Machinery room exhaust shall vent to the outdoors no fewer than 20 ft (6 m) from a property line or openings into buildings.
6.14.3.5
Machinery room exhaust shall discharge vertically upward with a minimum discharge velocity of 2,500 ft/min (762 m/min) at the required emergency ventilation flow rate.
6.14.3.6
Machinery room exhaust fans, regardless of function, shall be equipped with nonsparking blades.
6.14.3.7
*Emergency exhaust fan motors located in the air stream or inside the machinery room shall be of the totally enclosed type. Fan motors meeting this requirement are not required to be listed for use in hazardous (classified) locations.
6.14.4 Fan Options.
Multiple fans or multispeed fans shall be permitted to provide both temperature control exhaust ventilation in accordance with Section 6.14.6 and emergency exhaust ventilation in accordance with Section 6.14.7. Fans used for both temperature control and emergency ventilation shall be controlled in a manner that provides equal to or greater than the emergency ventilation rate when emergency ventilation is activated.
6.14.5 Inlet Air
6.14.5.1
Outdoor make-up air shall be provided to replace air being exhausted and shall maintain negative pressure in the machinery room, not to exceed 0.25 in. (6.4 mm) water column relative to the adjacent areas with a machinery room door, including the outdoors.
6.14.5.2
Make-up air supply locations in the machinery room shall be positioned to prevent short-circuiting of the make-up air directly to the exhaust.
6.14.5.3
Make-up air openings shall be covered with a corrosion-resistant screen of not less than ¼ in. mesh or equivalent protection.
6.14.5.4
Intakes for make-up air shall be positioned to draw uncontaminated outdoor air.
6.14.5.5
Intakes for make-up air to the machinery room shall serve only the machinery room.
6.14.5.6
Motorized louvers or dampers, where utilized, shall fail to the open position upon loss of power.
6.14.5.7
Where direct openings or openings with ducts are not provided to supply make-up air, make-up air shall be provided by fans or fans with ducts.
6.14.6 Temperature Control Ventilation
6.14.6.1
*Temperature control mechanical ventilation design capacity shall be the volume required to limit the room dry bulb temperature to 104°F (40°C), taking into account the ambient heating effect of machinery in the room and with the make-up air entering the room at a 1% design dry bulb temperature. The emergency ventilation system shall be permitted to be used to supplement temperature control ventilation, and vice versa. EXCEPTION: A reduced temperature control ventilation rate shall be permitted where a means of cooling is provided or room electrical equipment and wiring is designed to accommodate temperatures exceeding a dry bulb temperature of 104°F (40°C), in accordance with UL listings and the Electrical Code.
6.14.6.2
Partial operation of a multiple-fan system or multi-speed fans shall be permitted to deliver the temperature control ventilation design capacity.
6.14.6.3
Temperature control mechanical ventilation shall be continuous or shall be activated by both of the following: 1. A thermostat measuring space temperature. 2. A manual control switch provided in accordance with Section 6.12.2, where temperature control ventilation is designed to contribute to emergency ventilation.
6.14.7 Emergency Ventilation
6.14.7.1
*Emergency mechanical ventilation systems shall provide not less than 30 air changes per hour based on the gross machinery room volume. The emergency ventilation system shall be permitted to include temperature control ventilation fans that meet the requirements of Section 6.14.3.7 and Section 6.14.6.3, Item 2. EXCEPTION: Where approved, emergency mechanical ventilation shall not be required for a limited-charge refrigeration system that will not yield an ammonia concentration exceeding 40,000 ppm in the machinery room following a release of the entire charge from the largest independent refrigerant circuit, based on the volume calculation determined in accordance with Section 5.3. The designer shall provide a copy of the calculations to be retained at the site.
6.14.7.2
Emergency mechanical ventilation shall be activated by both of the following: 1. Ammonia leak detection complying with Section 6.13. 2. A manual control switch provided in accordance with Section 6.12.2.
6.14.7.3
Emergency ventilation shall be powered independently of the equipment within the machinery room and shall continue to operate regardless of whether emergency shutdown controls for the machinery room have been activated.
6.14.7.4
A monitored location shall be notified upon loss of power to or failure of the emergency mechanical ventilation system.
Chapter 17. Ammonia Detection and Alarms
17.1 Scope.
Ammonia leak detection and alarms located in “Machinery Rooms” shall comply with Section 6.13 and Sections 17.2–17.6 of this chapter. Ammonia leak detection and alarms in “Areas Other Than Machinery Rooms” shall comply with Section 7.2.3, Section 7.3.1.2.3, and this chapter. Ammonia leak detection and alarms for “Packaged Systems” shall comply with Section 14.4 and this chapter.
17.2 Power for Detectors and Alarms.
The power supply for the ammonia detectors and alarms shall be a dedicated branch circuit. In the event of a loss of power on other circuits or an emergency shutdown of refrigeration equipment, the ammonia detection and alarm system shall remain on. In the event of a loss of power to the ammonia detection and alarm system, a power failure trouble signal shall be sent to a monitored location.
17.3 Testing
17.3.1 Schedule.
A schedule for testing ammonia detectors and alarms shall be established based on manufacturers’ recommendations, unless modified based on documented experience.
17.3.2 Minimum Test Frequency.
Where manufacturers’ recommendations are not provided, ammonia detectors and alarms shall be tested at least annually.
17.4 Detector Placement
A leak detection sensor, or the inlet of a sampling tube that draws air to a leak detection sensor, shall be mounted in a position where ammonia from a leak is expected to accumulate. In rooms equipped with continuous exhaust ventilation, the location of leak detection sensors and sampling tubes shall take into account the air movement toward the inlet of the ventilation system. Leak detection sensors and sampling tube inlets shall be positioned where they can be accessed for maintenance and testing.
17.5 *Alarms.
The audible alarms providing notification shall provide a sound pressure level of 15 decibels (dBA) above the average ambient sound level and 5 dBA above the maximum sound level of the area in which it is installed.
17.6 Signage.
Ammonia leak detection alarms shall be identified by signage adjacent to visual and audible alarm devices.
17.7 Detection and Alarm Levels.
Where this standard specifies an ammonia detection and alarm concentration, the operational criteria shall be as specified in this section. EXCEPTION: Where approved, alternatives to fixed ammonia leak detectors shall be permitted for areas with high humidity or other harsh environmental conditions that are incompatible with detection devices.
17.7.1 Level 1 Ammonia Detection and Alarm.
Level 1 ammonia detection and alarm shall have the following features: 1. At least one ammonia detector shall be provided in the room or area. 2. The detector shall activate an alarm that reports to a monitored location so that corrective action can be taken at an indicated concentration of 25 ppm or higher.
17.7.2 Level 2 Ammonia Detection and Alarm.
Level 2 ammonia detection and alarm shall have the following features: 1. At least one ammonia detector shall be provided in the room or area. 2. The detector shall activate an alarm that reports to a monitored location so that corrective action can be taken at an indicated concentration of 25 ppm or higher. 3. Audible and visual alarms shall be provided inside the room to warn that, when the alarm has activated, access to the room is restricted to authorized personnel and emergency responders.
17.7.3 Level 3 Ammonia Detection and Alarm.
Level 3 ammonia detection and alarm shall have the following features: 1. At least one ammonia detector shall be provided in the room or area. 2. The detector shall activate an alarm that reports to a monitored location so that corrective action can be taken at an indicated concentration of 25 ppm or higher. 3. Audible and visual alarms shall be provided inside the room to warn that, when the alarm has activated, access to the room is restricted to authorized personnel and emergency responders. For machinery rooms, additional audible and visual alarms shall be located outside of each entrance to the machinery room. 4. Upon activation of the alarm, control valves feeding liquid and hot gas to equipment in the affected area shall be closed. Refrigerant pumps, nonemergency fans, or other motors that are part of the ammonia refrigeration equipment in the room shall be de-energized. 5. Upon activation of the alarm, emergency exhaust systems, where required, shall be activated.

## IIAR 2-2021
IIAR 2-2021 (2021-Present)
We would like to acknowledge and thank the International Institute of Ammonia Refrigeration (IIAR) for granting permission to include the following excerpts from its Standard 2-2021.
Summary of Key Ventilation Provisions
Chapter 5. General System Design Requirements
5.3 *Volume Calculation for Determining Concentration of an Ammonia Release.
For the purpose of applying Sections 4.2.2, 4.2.4, 5.15.3, 6.14.7, and Section 7.3.1.2, the volume used to calculate the potential ammonia concentration in the event of a release shall comply with this section. The volume used to calculate the potential ammonia concentration shall be the gross volume of a room or space into which released ammonia disperses based on the smallest gross volume in which the release will accumulate.
5.3.1 *Wall Openings.
Where spaces adjacent to those containing refrigeration systems, equipment, or portions thereof are connected by permanent wall openings, the volume of such adjacent spaces shall not contribute to the calculated volume used for ammonia release concentration calculations unless, based on the size and elevation of permanent wall openings or a mechanical ventilation system, the designer determines that migration and dilution of a release over the combined spaces will occur. The volume shall be the combined space, provided that the openings or mechanical ventilation are clearly identified as the basis for the design analysis.
5.3.2 Spaces Above Suspended Ceilings.
The space above a suspended ceiling shall not be included in the volume calculation unless the space above the ceiling functions as part of the air distribution system.
5.3.3 *Interconnected Floor Levels and Mezzanines.
Where a refrigeration system, or portion thereof, is located in a room or space containing multiple floor levels connected through an open atrium or where a mezzanine is open to a room or space, the combined volume of interconnected floors and mezzanines is permitted in the volume calculation.
5.3.4 *Mechanical Ventilation Considerations.
Where a refrigeration system, or portion thereof, is located 1) in an area served by a mechanical ventilation system that also serves additional spaces, 2) within an air handler, or 3) in an air distribution duct system, the volume of the rooms or spaces connected by the ventilation or duct system, including the volume of the connected supply and return air ducts exterior to the room and any connecting plenum, shall be used. EXCEPTION: The smaller of the volumes on either side of a damper shall be used where portions of the ventilation or duct system are subject to being isolated by dampers, other than 1) fire dampers, 2) smoke dampers, 3) combination fire and smoke dampers, or 4) dampers that continuously maintain not less than 10% airflow.
Chapter 6. Machinery Rooms
6.5 Open Flames and Hot Surfaces
Fuel-burning appliances and equipment and surfaces with temperatures exceeding 800°F (427°C) shall not be installed in a machinery room. EXCEPTIONS: 1. Fuel-burning appliances and equipment shall be permitted in a machinery room where combustion air to the fuel-burning appliance is ducted from outside of the machinery room and sealed to prevent ammonia leakage from reaching the combustion chamber. 2. Fuel-burning appliances and equipment shall be permitted in a machinery room where an ammonia detector is in accordance with Section 6.13 and automatically shuts off the combustion process upon detection of ammonia. 3. Internal combustion engines powering compressors shall be permitted in a machinery room.
6.8 Electrical Safety
6.8.1 Hazardous (Classified) Locations.
Machinery rooms are permitted to be designated as Unclassified Locations, as described in the electrical code, where the machinery room is provided with emergency ventilation in accordance with Section 6.14.7 and ammonia detection in accordance with Section 6.13. A machinery room not provided with emergency ventilation that is either operated continuously or activated by ammonia detector shall be designated as not less than a Class I, Division 2, Group D Hazardous (Classified) Location, and electrical equipment installed in the machinery room shall be designed to meet this requirement. EXCEPTION: Machinery rooms not provided with emergency ventilation but contain only refrigeration systems that are compliant with Section 6.14.7.1, Exception 1, are not required to be designated as a Class I, Division 2, Group D Hazardous (Classified) Location.
6.12 *Emergency Control Switches
6.12.2 Emergency Ventilation Control Switch.
A clearly identified control switch for emergency ventilation that is not operated continuously shall be located outside the machinery room and adjacent to the designated principal machinery room door. The switch shall provide “ON/AUTO” override capability for emergency ventilation. The function of the switch shall be clearly marked by signage near the controls. The switch shall be readily operable.
6.13 Ammonia Detection and Alarm
6.13.1 General
Machinery rooms shall be provided with a minimum of two (2) ammonia detectors and an alarm in accordance with Sections 17.2–17.6 and shall have the following features: 1. At least two ammonia detectors that have identical concentration sensing ranges shall beprovided in the room or area that detect concentrations and initiate the alarm sequences in accordance with 6.13.2.2 and 6.13.2.3. ANSI/IIAR 2 Standard for Design of Safe Closed-Circuit Ammonia Refrigeration Systems 23 2. Audible and visual alarms shall be provided inside the room to warn that access to the room is restricted to authorized personnel and emergency responders when the alarm has activated. Additional audible and visual alarms shall be located outside of each entrance to the machinery room. EXCEPTION: The use of a single detector is permitted if the failure or maintenance of the detector that causes the detection system to become inoperable, starts the emergency ventilation system that shall continue to operate until the detection system is restored. Failure of the emergency ventilation system to operate at the emergency ventilation rate shall initiate the alarm, notification and equipment shutdown described in Section 6.13.2.4.
6.13.2 Alarm Response
6.13.2.1
Detection of ammonia concentrations less than 25 ppm requires no alarm.
6.13.2.2
*Detection of ammonia concentrations equal to or exceeding 25 ppm shall activate visual indicators, audible alarms, and provide a notice to a monitored location. The visual indicator and audible alarm shall be permitted to reset automatically if the ammonia concentration drops below 25 ppm.
6.13.2.3
*Detection of ammonia concentrations equal to or exceeding 150 ppm (1/2 IDLH) shall activate visual indicators and an audible alarm and shall activate emergency ventilation, where such is required in accordance with Section 6.14.7. Once activated, emergency ventilation, and visual indicators shall continue to operate until manually reset by a switch located in the machinery room. Audible alarms shall continue to operate until they are manually reset by a switch located in the machinery room or alternatively in an area remote from the machinery room.
6.13.2.4
*Detection of ammonia concentrations that exceed a detector’s upper detection limit or 40,000 ppm (25% LFL), whichever is lower, shall activate visual indicators and an audible alarm and shall activate emergency ventilation where such is required in accordance with Section 6.14.7. If the detectors within the machinery room have more than one sensing range, the detector with the highest range of detection capability is permitted to be used to activate this alarm response. Once activated, emergency ventilation, and visual indicators shall continue to operate until being manually reset by a switch located in the machinery room. Audible alarms shall continue to operate until they are manually reset by a switch located in the machinery room or alternatively in an area remote from the machinery room. In addition, the following equipment in the machinery room shall be automatically de-energized and shall remain de-energized until being manually reset: 1. Refrigerant compressors, 2. Refrigerant pumps, and 3. Normally closed automatic refrigerant valves that are not part of an emergency control system
6.14 Ventilation
6.14.1 *Ventilation for Occupants.
During occupied conditions, outdoor air shall be provided at a rate of not less than 0.5 cfm/ft2 (0.0025 m3/s • m2) of machinery room area or 20 cfm (0.009 m3/s) per occupant, whichever is greater.
6.14.2 General Ventilation and Air Conditioning Equipment.
Machinery room ventilation fans and air conditioning equipment that are not part of an emergency ventilation system shall be automatically de-energized and associated fan dampers, where provided, shall automatically close upon detection of ammonia in accordance with Section 6.13.2.3. EXCEPTION: Exhaust fans that are not designated as emergency exhaust fans are permitted to remain energized upon detection of ammonia in accordance with Section 6.13.2.3. Such exhaust fans shall be in accordance with Sections 6.14.3.2 through 6.14.3.6.
6.14.3 Exhaust Ventilation.
Machinery rooms shall be vented to the outdoors by means of a mechanical exhaust ventilation system.
6.14.3.1
*Mechanical exhaust ventilation systems shall be designed to produce not less than the greater of (1) temperature control ventilation rate required by Section 6.14.6 or (2) the emergency exhaust ventilation rate required by Section 6.14.7.
6.14.3.2
Exhaust air ducts from the machinery room shall serve only the machinery room.
6.14.3.3
*Machinery room exhaust shall be to the outdoors not less than 20 ft (6 m) from a property line or openings into buildings. EXCEPTION: Machinery room exhaust is permitted to be installed within 20 ft. (6m) of tight-fitting machinery room doors and roof hatches that are not designated for emergency egress and that have signage indicating they must be closed after passage.
6.14.3.4
Machinery room emergency exhaust shall discharge vertically upward with a minimum discharge velocity of 2,500 ft/min (762 m/min) at the required emergency ventilation flow rate.
6.14.3.5
*Emergency exhaust fans shall be constructed such that radial or axial displacement of the impeller or shaft will not permit two ferrous parts of the fan to rub or strike.
6.14.3.6
*Emergency exhaust fan motors located in the air stream or inside the machinery room shall be of the totally-enclosed type. Fan motors meeting this requirement are not required to be listed for use in hazardous (classified) locations.
6.14.4 Fan Options.
Multiple fans or multispeed fans shall be permitted to provide both temperature control exhaust ventilation in accordance with Section 6.14.6 and emergency exhaust ventilation in accordance with Section 6.14.7. Fans used for both temperature control and emergency ventilation shall be controlled in a manner that provides equal to or greater than the emergency ventilation rate when emergency ventilation is activated.
6.14.5 Inlet Air
6.14.5.1
*Outdoor make-up air shall be provided to replace air being exhausted. The ventilation system(s) shall be designed to maintain negative pressure in the machinery room when exhaust fans are operating. The negative pressure shall not exceed 0.25 in. (6.4 mm) water column relative to the adjacent areas with a machinery room door, including the outdoors.
6.14.5.2
Make-up air supply locations in the machinery room shall be positioned to prevent short-circuiting of the make-up air directly to the exhaust.
6.14.5.3
Make-up air openings shall be covered with a corrosion-resistant screen of not less than ¼ in. mesh or equivalent protection. EXCEPTION: A smaller screen mesh or air filters are permitted to be installed if engineering or administrative controls are in place to ensure that the maximum negative air pressure requirement in Section 6.14.5.1 and the air quantity requirements in Sections 6.14.1, 6.14.6 and 6.14.7 are met.
6.14.5.4
Intakes for make-up air to the machinery room shall serve only the machinery room.
6.14.5.5
*Motorized louvers or dampers that are used for emergency ventilation systems shall fail to the open position upon loss of power.
6.14.5.6
Where direct openings or openings with ducts are not provided to supply make-up air, make-up air shall be provided by fans or fans with ducts.
6.14.6 Temperature Control Ventilation
6.14.6.1
*Temperature control mechanical ventilation design capacity shall be the volume required to limit the room dry-bulb temperature to 104°F (40°C), taking into account the ambient heating effect of equipment in the room and with the make-up air entering the room at the annual 1% design dry-bulb temperature. The emergency ventilation system shall be permitted to be used to supplement temperature control ventilation, and vice versa. EXCEPTION: A reduced temperature control ventilation rate shall be permitted where a means of cooling is provided, or room electrical equipment and wiring is designed to accommodate temperatures exceeding a dry-bulb temperature of 104°F (40°C), in accordance with UL Listings and the electrical code.
6.14.6.2
Partial operation of a multiple-fan system or multispeed fans shall be permitted to deliver the temperature control ventilation design capacity.
6.14.6.3
Temperature control mechanical ventilation shall be continuous or shall be activated by both of the following: 1. A thermostat measuring space temperature; and 2. A manual control switch provided in accordance with Section 6.12.2, where temperature control ventilation is designed to contribute to emergency ventilation.
6.14.7 Emergency Ventilation
6.14.7.1
*Emergency mechanical ventilation systems shall provide not less than 30 air changes per hour based on the gross machinery room volume. The emergency ventilation system shall be permitted to include temperature control ventilation fans that meet the requirements of Section 6.14.3 and Section 6.14.6.3, Item 2. EXCEPTIONS: 1. Where not prohibited by the AHJ, emergency mechanical ventilation shall not be required for a refrigeration system that will not yield an ammonia concentration exceeding 40,000 ppm in the machinery room following a release of the entire charge from the largest independent refrigerant circuit, based on the volume calculation determined in accordance with Section 5.3. The designer shall provide a copy of the calculations to be retained at the site. 2. A reduced emergency ventilation rate is permitted where an engineering analysis indicates that the reduced rate will prevent an ammonia concentration from exceeding 40,000 ppm in the machinery room following a release of the entire charge from the largest independent circuit in the room. The analysis must be documented and retained on-site.
6.14.7.2
Operation of emergency ventilation that is not operated continuously shall be initiated by the ammonia detection system in accordance with Section 6.13.
6.14.7.3
Emergency ventilation that is not continuously operated shall also be operable manually by emergency control switches in accordance with Section 6.12.2
6.14.7.4
Emergency ventilation shall be powered independently of the equipment within the machinery room and shall continue to operate regardless of whether emergency shutdown controls for the machinery room have been activated.
6.14.7.5
A monitored location shall be notified upon loss of power to the emergency mechanical ventilation system.
6.14.7.6
*A means of proving emergency airflow shall be provided. The means of proving emergency airflow shall be capable of sensing a change in air flow of 25% or more, either by direct airflow measurement or indirect sensor readings. Failure to prove airflow when the emergency ventilation fans are energized shall provide notice to a monitored location. Devices that can be used to prove emergency airflow include but are not limited to: 1) pressure differential switches 2) sail switches 3) current monitors.
Chapter 17. Ammonia Detection and Alarms
17.1 *Scope.
Ammonia leak detection and alarms located in “Machinery Rooms” shall comply with Section 6.13 and Sections 17.2–17.6 of this chapter. Ammonia leak detection and alarms in “Areas Other than Machinery Rooms” shall comply with Section 7.2.3 or Section 7.3.1.2.3, as applicable, and this chapter. Ammonia leak detection and alarms for “Packaged Systems” shall comply with Section 14.4 and this chapter.
17.2 Installation Design Requirements.
17.2.1 Power Supply.
In the event of an emergency shutdown of refrigeration equipment, the ammonia detection and alarm system shall remain on. Leak detection and alarm system power shall remain on during all refrigeration equipment maintenance procedures. In the event of a loss of power to the ammonia detection system and/or alarm system a power failure trouble signal shall be sent to a monitored location.
17.2.2 Wire Runs.
Detectors shall use supervised wire runs such that any faults in the wiring are reported to a monitored location.
17.2.3 Communication.
Loss of communication between the detector and the control system(s) that enables response shall be reported to a monitored location.
17.2.4 Monitoring Sensing Element(s).
Detectors shall actively monitor the primary sensing element(s) and report any trouble signal to a monitored location.
17.3 Design and Testing Standards.
Ammonia detectors shall be designed and tested in accordance with UL-61010-1 “Safety Requirements for Electrical Equipment for Measurement, Control, and Laboratory Use” or ANSI/ISA 92.00.01 “Performance requirements for Toxic Gas Detectors”.
17.4 *Detector Placement.
A leak detection sensor, or the inlet of a sampling tube that draws air to a leak detection sensor, shall be mounted in a position where it is expected to be the most effective. Leak detection sensors and sampling tube inlets shall be positioned where they can be accessed for maintenance and testing.
17.5 *Alarms.
The audible alarms providing notification shall provide a sound pressure level of 15 decibels (dBA) above the average ambient sound level and 5 dBA above the maximum sound level of the area in which it is installed.
17.6 Signage.
Ammonia leak detection alarms shall be identified by signage adjacent to visual and audible alarm devices.
17.7 *Detection and Alarm Levels.
Where this standard specifies an ammonia detection and alarm concentration, the operational criteria shall be as specified in this section.
17.7.1 Level 1 Ammonia Detection and Alarm.
Level 1 ammonia detection and alarm shall have the following features: 1. At least one ammonia detector shall be provided in the room or area, and 2. The detector shall activate an alarm that reports to a monitored location so that corrective action is taken at an indicated concentration of 25 ppm or higher.
17.7.2 Level 3 Ammonia Detection and Alarm.
Level 3 ammonia detection and alarm shall have the following features: 1. At least one ammonia detector shall be provided in the room or area. 2. The detector shall activate an alarm that reports to a monitored location so that corrective action can be taken at an indicated concentration of 25 ppm or higher. 3. Audible and visual alarms shall be provided inside the room to warn that, when the alarm has activated, access to the room is restricted to personnel authorized to respond to alarms and emergency responders. 4. Upon activation of the alarm, control valves feeding liquid and hot gas to equipment in the affected area shall be closed. Refrigerant pumps, nonemergency fans, or other motors that are part of the ammonia refrigeration equipment in the room shall be de-energized. 5. Upon activation of the alarm, emergency exhaust systems, where required, shall be activated.

## IIAR 9-2020
IIAR 9-2020 (2020-Present)
We would like to acknowledge and thank the International Institute of Ammonia Refrigeration (IIAR) for granting permission to include the following excerpts from its Standard 9.
Summary of Key Ventilation Provisions
7.3 General Machinery Room Requirements
7.3.5 Open Flames and Hot Surfaces..
Fuel-burning appliances and equipment and surfaces with temperatures exceeding 800°F (427°C) shall not be installed in a machinery room. EXCEPTIONS: 1. Fuel-burning appliances and equipment shall be permitted in a machinery room where combustion air to the fuel-burning appliance is ducted from outside of the machinery room and sealed to prevent ammonia leakage from reaching the combustion chamber. 2. Fuel-burning appliances and equipment shall be permitted in a machinery room where an ammonia detector is in accordance with Section 7.3.12 and automatically shuts off the combustion process upon detection of ammonia. 3. The use of matches, lighters, sulfur sticks, welding equipment, and similar portable devices shall be permitted except when charging is being performed and when oil or ammonia is being removed from the system. 4. Internal combustion engines powering compressors shall be permitted in a machinery room.
7.3.11 *Emergency Control Switches
7.3.11.2 Emergency Ventilation Control Switch.
A clearly identified control switch for emergency ventilation with a tamper-resistant cover shall be located outside the machinery room and adjacent to the designated principal machinery room door unless the continuous ventilation operates at a rate at or above that required for emergency ventilation. The switch shall provide “ON/AUTO” override capability for emergency ventilation. The function of the switch shall be clearly marked by signage near the controls.
7.3.12 *Ammonia Detection and Alarms
7.3.12.1 General.
Machinery rooms shall be provided with ammonia detection and alarms with the following features: 1) At least one ammonia detector shall be provided in the room or area. 2) The detector shall activate an alarm that reports to a monitored location so that corrective action can be taken. 3) Audible and visual alarms shall be provided inside the room. Additional audible and visual alarms shall be located outside of each entrance to the machinery room.
7.3.12.2 Alarm Response.
At a minimum, the machinery room alarm response shall be at an appropriate arrangement for the following to occur: 1) Activates an alarm to a monitored location so an immediate response can be set in place at a detected concentration of no higher than 50 ppm. 2) *Activate emergency ventilation at a detected concentration of no higher than 1000 ppm. 3) Automatically de-energize determined equipment at a detected concentration no higher than 40,000 ppm (25% LFL). At a minimum, the determined equipment shall include the following: the refrigerant compressors; refrigerant pumps; and normally closed automatic refrigerant valves that are not part of an emergency control system.
7.3.12.3 Power for Detectors and Alarms.
The power supply for the ammonia detectors and alarms shall be a dedicated branch circuit. In the event of a loss of power on other circuits or an emergency shutdown of refrigeration equipment, the ammonia detection and alarm system shall remain on. In the event of a loss of power to the ammonia detection and alarm system, a power failure trouble signal shall be sent to a monitored location.
7.3.12.4 Detector Placement.
A leak detection sensor, or the inlet of a sampling tube that draws air to a leak detection sensor, shall be mounted in a position where ammonia from a leak is expected to accumulate. In rooms equipped with continuous exhaust ventilation, the leak detection sensors and sampling tubes shall take into account the air movement toward the inlet of the ventilation system. Leak detection sensors and sampling tube inlets shall be positioned where they can be accessed for maintenance and testing.
7.3.12.5 Alarms.
The audible alarms providing notification shall provide a sound pressure level of 15 decibels (dBA) above the average ambient sound level and 5 dBA above the maximum sound level of the area in which it is installed.
7.3.12.6 Signage.
Ammonia leak detection alarms shall be identified by signage adjacent to visual and audible alarm devices.
7.3.13 Ventilation
7.3.13.1 *Ventilation for Occupants.
In occupied conditions, outdoor air shall be provided at a rate that complies with the codes and standards adopted at the time of installation or at the time that there was an addition or modification that would affect the occupancy ventilation rate.
7.3.13.2 Exhaust Ventilation
Machinery rooms shall be vented to the outdoors by means of a mechanical exhaust ventilation system at a rate that complies with the codes and standards adopted at the time of installation or at the time that there was an addition or modification that would affect the emergency ventilation rate. 1) Mechanical exhaust ventilation system shall be automatically activated by ammonia leak detection in accordance with Section 7.3.12.2 and shall be manually operable. 2) Machinery room exhaust fans, regardless of function, shall be equipped with non-sparking blades. 3) Emergency exhaust fan motors located in the air stream or inside the machinery room shall be of the totally enclosed type. 4) A monitored location shall be notified upon loss of power to, or failure of, the emergency mechanical ventilation system.
7.3.13.3 Inlet Air
1) Make-up air shall be provided to replace air being exhausted. 2) Make-up air supply locations in the machinery room shall prevent shortcircuiting of the make-up air directly to the exhaust. 3) Intakes for make-up air shall draw uncontaminated outdoor air. 4) Intakes for make-up air to the machinery room shall serve only the machinery room. 5) Motorized louvers or dampers, where utilized, shall fail to the open position upon loss of power. 6) Where direct openings or openings with ducts are not provided to supply makeup air, make-up air shall be provided by fans or fans with ducts.
7.4 General Equipment Safety Requirements
7.4.2 Atmospheric Discharge from Pressure Relief Devices.
If the pressure relief devices discharge vapor directly to the atmosphere outdoors, they shall comply with the following: 7.4.2.1 The termination of pressure relief device discharge piping relieving to the atmosphere shall not be less than 15 ft (4.6 m) above grade and not less than 20 ft (6.1 m) from windows, ventilation intakes, or exits.